## Slide 1
SWRO DESALINATION and VRF SYSTEMS
DESIGN FOR A COASTAL HOTEL
Presented by :
  Abdelrahman Ahmed Mosa Abd Elgawad
  Ahmed Adel Youssef Selim
  Amr El Sakar
Supervised by : Dr. Mohamed Shawky

## Slide 2
SWRO DESALINATION SYSTEM

## Slide 3
Hotel Demand
The hotel has 118 rooms
1 m3/room per day
Hotel Demand = 118 m3/day.
Hotel Demand * fos = 141.6 m3/day.

## Slide 4
RO Feed Quality Guidelines
Analysis Input Data
VEOLIA Winflows Analysis
Analysis Results for Feed, Brine, and Permeate Water
Drinking Water Quality Guidelines

## Slide 5
Pre-Treatment

## Slide 6
Procedure
Chlorination
Coagulation
Multimedia Filtration
VEOLIA FIB-125

## Slide 7
Procedure
Softener
Cartridge Filter
VEOLIA AZ350
PENTAIR housing CFHF filters
SMBS

## Slide 8
Membrane (Core)
40% Design Recovery Rate within 35~50 Range
Product Flow Rate 141.6 m3/day
Flux 9.2 GFD within 8~12 Range
TDS Reduced from 35,153.95 to 246.89 mg/L
2x6 VEOLIA AE-400-34 Membranes

## Slide 9
Pressure Vessels
670 psi Inside Pressure
7.9 Inches Element Diameter
2 Pressure Vessels SNOWATE F80-1000E-6W

## Slide 10
Post-Treatment

## Slide 11
Procedure
Chlorination
Remineralization
LENNTECH Calcite Filtration Media

## Slide 12
Pipe Sizing
Low Pressure
High Pressure

## Slide 13
Check Valve
Flow Control Valve
Isolation Valve
Valves

## Slide 14
Pressure Gauge
Flow Meter
Measuring Devices
PH Meter

## Slide 15
Tanks
Raw Water Tank
IZOPLAS Vertical Fiberglass Tank
Underground Permeate Storage Tank
Nationwide Gen2 Underground Fiberglass Tank

## Slide 16
Pumps
GRUNDFOS SP 18-3
Q = 4.4 L/s
H = 25.3 m
Well Submersible Pump
GRUNDFOS NK 40-125116
Low Pressure Feed Pump
Q = 4.2 L/s
H = 2.2 m
GRUNDFOS BMS 18-22
High Pressure Feed Pump
Q = 4.11 L/s
H = 468.7 m

## Slide 17
Electricity Cost Analysis
Power Demand
39.07 kW
Energy Consumption
937.79 kWh/day
Fresh Water Output
141.6 m³/day
Global Operating Cost
1.053 USD/m³
Local Operating Cost
14.737 LE/m³

## Slide 18
Normal Operation

## Slide 19
Backwash
Backwash Cycle
Rinse Cycle

## Slide 20
Cleaning

## Slide 21
Plant P&ID
Normal Operation
Backwash
Cleaning

## Slide 22
VRF SYSTEM

## Slide 23
Load Estimation

## Slide 24
Carrier HAP
Weather
Properties

## Slide 25
Carrier HAP
Architectural
Configurations

## Slide 26
Carrier HAP
East
Mid
West
Kitchen
Unconditioned

## Slide 27
Carrier HAP
Air Systems

## Slide 28
Load Design Results Sample

## Slide 29
System Design
VRF
~0% FAR
DOAS
100% FAR
+

## Slide 30
Components Selection

## Slide 31
VRF Indoor Units
Four Way Cassette
Two Way Cassette
Concealed Duct Unit

## Slide 32
VRF Indoor Units

## Slide 33
VRF Outdoor Units

## Slide 34
DOAS

## Slide 35
Kitchen Zone
Double
Island
Canopy

## Slide 36
DX-AHU

## Slide 37
Duct Sizing

## Slide 38
ESP and Fan Selection
East-Side Fan
West-Side Fan

## Slide 39
Shop drawing

## Slide 40
THANK YOU!